(888) 338 - 5225; WWW.CAPTIVEAIRE.COM.

Wednesday, September 25, 2024; Quote# 7063622 - A&W MODERNIZATION - Napanee ON.

To: MECH; From: Reed Brown. CaptiveAire Systems. 114 NW Canal St. #300. Seattle, WA 98107. Local: (425) 212 - 5996. Toll Free: (888) 338 - 5225. Fax: (425) 212 - 5998. reg85@captiveaire.com.; Ship To: A&W. 638 County Road 41. Greater Napanee, ON K0K 2Z0. CANADA..

CaptiveAire Systems proposes to furnish the following equipment. Production of listed items will commence upon receipt of an approved proposal, a purchase order, an approved submittal and approved credit.

EQUIPMENT:

| Fan #1 DU180HFA - Exhaust Fan (EF-1W) - Job #7063622 |  |  |  |
| --- | --- | --- | --- |
| DU180HFA High Speed Direct Drive Centrifugal Upblast Exhaust Fan with, disconnect switch and 18-3/4" wheel. Exhaust Fan handles 1200 CFM @ -1.400" wc ESP, Fan runs at 1120 RPM. Exhaust Motor: 1.000 HP, 3 Phs, 575 V, 60 Hz, 1.3 FLA, ODP, Premium (E-Plus3) Eff. |  | x1 |  |
| - Grease Cup for kitchen-duty centrifugal exhaust fans, Box Dimensions 17-1/8 L X 5-1/16 W X 3-3/4 H (20 Gauge) (Includes Down Spout) |  | x1 |  |
| - Full crating for exhaust fans for shipping. Crating for Export. |  | x1 |  |
| - DU/DR180HFA Gasketing Kit - Thermeez Woven Ceramic Tape - 1/4" x 1" with adhesive back - Max Temp 1500°F. To be applied between fan base and grease duct. Installed under fan base 1/2" from the inside. Installed at the plant. |  | x1 |  |
| - Mount Load Reactor in Fan. |  | x1 |  |
| - KDRMA45L1 - 600V 2.1A Line/Load reactor. Used with VFD. Use VFD spreadsheet to determine which VFD HP can be associated with reactor. Replacing: PN: RM0002M20 |  | x1 |  |
| - EF-1W Curb CRB26.5x24E On Fan #1 Flat Curb |  | x1 |  |
| - Hinged Base for Curb. Standard Hinge attached to curb. Used on Fans with wheels 20 inches or smaller. 12 GA Galvanized. |  | x1 |  |
| - Vented Base for Curb |  | x1 |  |
| Fan Total Price: |  |  | C$2,263.35 |

| Fan #2 DU180HFA - Exhaust Fan (EF-2W) - Job #7063622 |  |  |  |
| --- | --- | --- | --- |
| DU180HFA High Speed Direct Drive Centrifugal Upblast Exhaust Fan with, disconnect switch and 18-3/4" wheel. Exhaust Fan handles 1200 CFM @ -1.400" wc ESP, Fan runs at 1120 RPM. Exhaust Motor: 1.000 HP, 3 Phs, 575 V, 60 Hz, 1.3 FLA, ODP, Premium (E-Plus3) Eff. |  | x1 |  |
| - Grease Cup for kitchen-duty centrifugal exhaust fans, Box Dimensions 17-1/8 L X 5-1/16 W X 3-3/4 H (20 Gauge) (Includes Down Spout) |  | x1 |  |
| - Full crating for exhaust fans for shipping. Crating for Export. |  | x1 |  |
| - DU/DR180HFA Gasketing Kit - Thermeez Woven Ceramic Tape - 1/4" x 1" with adhesive back - Max Temp 1500°F. To be applied between fan base and grease duct. Installed under fan base 1/2" from the inside. Installed at the plant. |  | x1 |  |
| - Mount Load Reactor in Fan. |  | x1 |  |
| - KDRMA45L1 - 600V 2.1A Line/Load reactor. Used with VFD. Use VFD spreadsheet to determine which VFD HP can be associated with reactor. Replacing: PN: RM0002M20 |  | x1 |  |
| - EF-2W Curb CRB26.5x24E On Fan #2 Flat Curb |  | x1 |  |
| - Hinged Base for Curb. Standard Hinge attached to curb. Used on Fans with wheels 20 inches or smaller. 12 GA Galvanized. |  | x1 |  |
| - Vented Base for Curb |  | x1 |  |
| Fan Total Price: |  |  | C$2,263.35 |

| Fan #3 A2-D.250-20D-MPU - Heater (MUA-1) - Job #7063622 |  |  |  |
| --- | --- | --- | --- |
| A2-D.250-20D-MPU Direct Gas Fired Heated Make Up Air Unit with 20" Mixed Flow Direct Drive Fan Supply Fan handles 2300 CFM @ 0.460" wc ESP, Fan runs at 1221 RPM. Heater supplies 186396 BTUs. 77°F Temperature Rise. [Fuel: Natural Gas] Supply Motor: 2.000 HP, 3 Phs, 575 V, 60 Hz, 2.3 FLA, ODP, Premium (E-Plus3) Eff. Down Discharge - Air Flow Right -> Left |  | x1 |  |
| - Sloped Filtered Intake for Size #2 Modular Heater. 26.813" Wide X 53.625" Long X 31.313" High. Includes 2" MV EZ Kleen Metal Mesh Filters. |  | x1 |  |
| - 0-150°F Discharge Temp Control • Field Wired On/Off Start Command • Heating Activation Based On Intake Set Point. Use with MUA |  | x1 |  |
| - Gas Manifold for DF2 GM - BTU 0 - 825001 - 7 in. w.c. - 14 in. w.c., No Insurance Requirement (ANSI), BV250-88 |  | x1 |  |
| - Profile Plate Configuration for size 2 Direct Fired Unit for low cfm applications. |  | x1 |  |
| - Gas Pressure Gauge, 0-35", 2.5" Diameter, 1/4" Thread Size |  | x1 |  |
| - Gas Pressure Gauge, -5 to +15 Inches Wc., 2.5" Diameter, 1/4" Thread Size |  | x1 |  |
| - Butterfly Mod Valve Option for Mod Size 2 (1" Mod Valve). |  | x1 |  |
| - Ship Loose Gas Strainer. To be installed upstream of unit connection. 1" Connection |  | x1 |  |
| - Pilot located upstream of First Redundant Solenoid Valve of size 1-3 Max Gas Pressure of 14" wc. |  | x1 |  |
| - Motorized Back Draft Damper 22.75" X 24" for Size 2 Standard & Modular Heater Units w/Extended Shaft, Standard Galvanized Construction, 3/4" Rear Flange, Low Leakage, LF120S Actuator Included |  | x1 |  |
| - Control panel enclosure heater, includes 100w, 120v heater. Recommended for winter design temperature less than 0°F. Operates on PCB controls in IBT Single Modules or RTU |  | x1 |  |
| - Full crating for commercial heaters for shipping. Crating for Export. |  | x1 |  |
| - 10 Ton, Dual Circuit (5/5) Modular Packaged AC Cooling Option for Size 2 DF/EH Modular Packaged Unit. Includes Condenser, DX Coil, Filter/Dryer Kit, Thermal Expansion Valve, R410A Refrigerant, and Refrigerant Piping. (1500 to 3,000 cfm) When ordered with opposite airflow condensers access and coil piping will remain in standard position. Drain and sleds will move to the opposite side. Any other change will require CLI. CONDENSERS REQUIRE SEPARATE 575V, 3 PHASE POWER SUPPLY UNLESS ORDERED WITH SINGLE POINT CONNECTION. Coil = 3EY1203 |  | x1 |  |
| - Downturn Plenum for Size 2 Cooling Coil Module - Required for Down Discharge Cooling Coil Applications |  | x1 |  |
| - Single Point MPU Connection, 2 Condensers. |  | x1 |  |
| - Freezestat |  | x1 |  |
| - GFCI 15 amp Convenience Outlet For Heater Enclosure. Power supply by others - Includes receptacle and J box. |  | x1 |  |
| - Unit mounted VFD For use with ECPM03 |  | x1 |  |
| - Mount Load Reactor in Fan. |  | x1 |  |
| - ESV152N06TXB571 - Variable Frequency Drive - 2 HP Max., 600 V, Three Phase, 2.7 A Max., NEMA 1 Enclosure, with 2RJ-45 FOR MODBUS |  | x1 |  |
| - CAT5_Regular_100 - CAT-5E CABLE - 100 Foot. UV Rated. |  | x1 |  |
| - KDRMA47L1 - 600V 3.2A Line/Load reactor. Used with VFD. Use VFD spreadsheet to determine which VFD HP can be associated with reactor. Replacing: PN: RM0004M12 |  | x1 |  |
| - ROGERS CELLULAR KIT, WIRED ANTENNA AND ROGERS DATA FOR 3 YEARS. USED WITH FAN. |  | x1 |  |
| - MUA-1 Curb CRB31X145X20INS Insulated On Fan #3 Flat Curb |  | x1 |  |
| - Full Bottom Curb Corner. Base flange corners fully welded or staked by factory. |  | x1 |  |
| Fan Total Price: |  |  | C$25,220.14 |

| Electrical System #1 - Job #7063622 |  |  |  |
| --- | --- | --- | --- |
| DCV-2111 Demand Control Ventilation, w/ control for 2 Exhaust Fans, 1 Supply Fan, Exhaust on in Fire, Lights out in Fire, Fans modulate based on duct temperature. INVERTER DUTY 3 PHASE MOTOR REQUIRED FOR USE WITH VFD. Room temperature sensor shipped loose for field installation.Verify distance between VFD and Motor; additional cost could apply if distance exceeds 50 feet. Includes 2 Duct Thermostat kits. |  | x1 |  |
| - ESV751N06TXB571 - Variable Frequency Drive - 1 HP Max., 600 V, Three Phase, 1.7 A Max., NEMA 1 Enclosure, with 2RJ-45 FOR MODBUS |  | x1 |  |
| - KDRMA45L1 - 600V 2.1A Line/Load reactor. Used with VFD. Use VFD spreadsheet to determine which VFD HP can be associated with reactor. Replacing: PN: RM0002M20 - Fan: 1 |  | x1 |  |
| - ESV751N06TXB571 - Variable Frequency Drive - 1 HP Max., 600 V, Three Phase, 1.7 A Max., NEMA 1 Enclosure, with 2RJ-45 FOR MODBUS |  | x1 |  |
| - KDRMA45L1 - 600V 2.1A Line/Load reactor. Used with VFD. Use VFD spreadsheet to determine which VFD HP can be associated with reactor. Replacing: PN: RM0002M20 - Fan: 2 |  | x1 |  |
| - 24 wide X 18 tall X 8.62 deep SS HINGED ELECTRICAL BOX NEMA 1 - VENTED. Includes fan filter assembly. -USED ON CONTROL PANELS WITH VFD(S). |  | x1 |  |
| - ROGERS CELLULAR KIT, WIRED ANTENNA AND ROGERS DATA FOR 3 YEARS. |  | x1 |  |
| - Digital Prewire Lighting Relay Kit. Includes hood lighting relay & terminal blocks. Allows for up to 1400W of lighting each. |  | x1 |  |
| - Thermistor CABLE - 18/2 AWG GREEN WHITE, plenum rated. USED for thermistor duct stat. Per Foot Price. |  | x100 |  |
| Electrical System #1 Total Price: |  |  | C$4,253.79 |

| CASLink Monitoring |  |  |  |
| --- | --- | --- | --- |
| CASLink Monitoring |  | x1 |  |
| CASLink Monitoring Total Price: |  |  | C$897.11 |

| Buyouts |  |  |  |
| --- | --- | --- | --- |
| - ***** USE HEMISPHERE BROKERAGE ***** • CONTACT: Joe (email: joe@hemispherebrokerage.com) • P(416) 252-5661 • F(416) 252-1286 |  | x1 |  |
| - QTY 2 STANDARD GREASE GUARDS FOR 26"SQ CURB AND SMALLER. **INCLUDES SHIPPING** |  | x1 |  |
| Buyouts Total Price: |  |  | C$4,002.71 |

| Factory Services |  |  |  |
| --- | --- | --- | --- |
| Service Design Verification for CASLink. |  | x1 |  |
| Service Design Verification for Demand Control Ventilation |  | x1 |  |
| Service Design Verification for Direct Fired Heater |  | x1 |  |
| Service Design Verification for Exhaust Fan |  | x2 |  |
| Service Design VerificationMileage Charge: (136.0) x 2 = 272.0 total miles |  | x1 |  |
| Factory Services Total Price: |  |  | C$1,282.43 |

| Subtotal: | C$40,182.88 |
| --- | --- |
| Shipping: | C$3,138.47 |
| HST: | C$5,631.73 |
| Total: | CAD C$48,953.08 |

SERVICE DESIGN VERIFICATION DISCLAIMER

Field Service Technician is responsible for one trip to site to ensure the above equipment is operating within design specifications. All equipment must be operational. Fire suppression system should be hooked-up and armed. Additional trips will result in charges to be covered by others.

| INSTALLATION BY OTHERS |  |
| --- | --- |
| Installation of these products should be performed by a qualitfied professional who has read and understands the product manuals and is familiar with the proper safety precautions. By Others: Installation, receiving, hanging and setting of equipment, ductwork, patching, all electrical field wiring, start-up & balance, gas or electric shutdown for fire system hook-up, field piping, detection and pull station line(s), tests and permits. Checking equipment for any signs of damage upon receipt, and if found, report it immediately to the carrier. Check that all items are accounted for and free of damage. Condenser, filter / dryer kit, refrigerant, condenser disconnect and expansion valve, for use with DX coil module, will all be provided, installed, started and warranted by others. Note: Customer is responsible for additional labor charges as a result of cooking equipment layout changes after the release of the order, union labor or prevailing wage charges, or additional trips by fire system distributor caused by jobsite delays, permits, fees or test required by local authority. Submittal will specify applicable testing and approval agencies. The fire suppression system final hook up is not included on this quote. The final hook up usually consists of, but is not limited to, field piping/re-piping, detection and pull station line(s), tests, and permits. Hook up for the fire system must be performed in accordance with the product manual by a Factory Trained Distributor. Failure to utilize a factory trained distributor voids the product warranty. | CaptiveAire Systems requirement for all field hook ups: All fire system installation materials and methods must be in accordance with the product manual, which includes but not limited to: fire system piping, gas shut-off valves, low-voltage wiring and conduit, verification of appliance coverage, and start-up and inspection procedures. CaptiveAire Systems product must be installed in accordance with installation instructions provided with equipment or available on our web site at www.captiveaire.com. Ductwork must be designed and installed in accordance with AMCA and ASHRAE standards as presented in CaptiveAire Systems "Guide to Designing Air Flow Systems", available here. Hood and Ductwork hanging brackets and angles must be supported with 1/2" - 13 TPI grade 5 (minimum) all-thread. Sandwich hanging angles and ceiling anchor points with 1/2" grade 5 (minimum) steel flat washers and 1/2" - 13 TPI grade 5 (minimum) hex nuts. A doubled hex nut configuration must be used beneath hood and duct hanging brackets and above ceiling anchors (single hex nut beneath hanging angle is only acceptable for full length and supply plenum hanging angle types). Maintain 1/4" of exposed threads beneath bottom hex nut. Torque all hex nuts to 57 ft-lbs. Reference the installation manual for additional details and limitations of all structural supports. |

WARRANTY

Standard Product Warranty

This equipment is warranted to be free from defects in materials and workmanship, under normal use and service, for a period of 2-years from date of shipment.

Warranty Instructions

This Standard Product Warranty shall not apply if: - The equipment is not installed by a qualified installer per the MANUFACTURER'S installation instructions shipped with the product. - The equipment is not installed in accordance with federal, state and local codes and regulations. - The equipment is misused or neglected, or not maintained per the MANUFACTURER'S maintenance instructions. - The equipment is not operated within its published capacity. - The invoice is not paid within the terms of the sales agreement. The MANUFACTURER shall not be liable for incidental and consequential losses and damages potentially attributable to malfunctioning equipment. Should any part of the equipment prove to be defective in material or workmanship within the Standard Product Warranty, upon examination by the MANUFACTURER, such part will be repaired or replaced by MANUFACTURER at no charge. The BUYER shall pay all labor costs incurred in connection with such repair or replacement. Equipment shall not be returned without MANUFACTURER'S prior authorization and all returned equipment shall be shipped by the BUYER, freight prepaid to a destination determined by the MANUFACTURER. NOTE: To receive warranty coverage, register this product by filling out the Start-up and Maintenance Document. Fax the form to 1-919-554-9374 or call 1-866-784-6900 for email information.

SHIPPING

Lift gates are not available from LTL shipping carriers for products over 96" in length.

Freight includes one shipment only, delivered to the job site address listed on this proposal. Customer is responsible for freight charges on any items shipped early. This is an estimated freight charge and is subject to change based on current freight costs when the job is released for production.

APPROVAL

The above prices, associated submittal drawings, specifications, and conditions are satisfactory and are hereby accepted. You are authorized to perform the work specified. Receipt of the CaptiveAire Systems Terms & Conditions are hereby acknowledged (Form TC101), and by signature hereto, we agree to said Terms & Conditions. Payment will be made in accordance with authorized agreement. Please note, proposal may be withdrawn by CaptiveAire Systems if not accepted within 30 days for immediate shipment. Authorized Signature; Date. Signature; Date. We accept MasterCard®, VISA®, American Express®, and Discover® cards for immediate credit approval and expedited order processing.

TERMS AND CONDITIONS

Acceptance: This proposal is submitted for acceptance within 30 days from the date of proposal. Prices are firm after acceptance -see paragraph "prices." Typographical and clerical errors in quotations, orders and acknowledgments are subject to correction. Terms of Payment: Net thirty (30) days from date of our invoice, unless specified to the contrary and subject to the approval of the Company. A Service Charge of 1.5 % per month may be invoked and applied after the 30 day period until payment is received. Invoicing will be rendered when shipment has been made, unless otherwise indicated in quotation. The stated price is subject to any state, federal or local government regulatory ordinances or statutes governing interest rates and shall be construed and interpreted to allow the highest rate applicable and not more. In the event of a conflict between this rate and other law, the law shall prevail. In the event CaptiveAire Systems employs an attorney to enforce its rights and remedies under this agreement and/or to collect funds owing pursuant to this agreement, buyer agrees to pay a reasonable attorney's fee for CaptiveAire Systems attorney, plus all other reasonable expenses incurred by CaptiveAire Systems in enforcing its rights under this agreement. Taxes: Unless specifically stated, we include no taxes of any kind in the sale price. Any taxes, if applicable and imposed by any present or future local, state or federal agency for any reason must be paid by the Buyer. Shipments: All shipments are f.o.b. Factory or, if shipped from another location, f.o.b., point of shipment with charges either allowed, added to invoice, or collect as noted. Claims: The responsibility of the company ceases upon delivery of material in good order to the carrier. As all goods are shipped at buyer's risk, any claims for damage or shortage or loss in transit must be filed by the buyer against the transportation company, (We will assist the Buyer in any reasonable way possible in the filing and collection for any claim for damages and/or losses while in transit.) Claims against factory shortages will not be considered unless made within 60 days after receipt of the goods. Acceptance or Approval: Should the equipment on this proposal be purchased subject to acceptance or approval of another (such as Architect, Engineer. Owner, etc.), CaptiveAire Systems shall not be liable in any way should acceptance or approval not be granted. We cannot guarantee to meet or equal specifications written on behalf of another equipment manufacturer. Warranties: CaptiveAire Systems extends to buyer the manufacturers warranty (a copy of which is available upon request). Manufacturer's warranty is in lieu of any warranties contained in any applicable project conditions, plans, or specifications unless specifically stated otherwise. CaptiveAire Systems makes no other warranties, express or implied, as to any matter whatsoever, including without limitation, the conditions of the equipment, its merchantability or fitness for a particular purpose. CaptiveAire Systems shall not be liable for any damages by reason of failure of the equipment to operate or a faulty operation of this equipment. CaptiveAire Systems shall not be held responsible for any direct, incidental or consequential damages or liquidated damages or losses (including but not limited to loss of use, income, profit or production, or spoilage or increased cost of operation) resulting from the installation, operation or use of the equipment. Limitation of Remedy: CaptiveAire Systems shall have no liability for any damage caused by negligence, accident, misuse, improper storage, improper installation, improper service, maintenance or operation. CaptiveAire Systems liability (whether under theories of warranty, negligence, strict liability or contract) is limited solely to repair or replacement of the equipment or its parts by CaptiveAire Systems or its duly authorized representative, or at CaptiveAire Systems option and in its sole discretion, refund of the purchase price, and the foregoing shall be the sole and exclusive remedy against CaptiveAire Systems. In no event shall CaptiveAire Systems liability with respect to the goods or their non-delivery exceed the purchase price paid by Buyer to CaptiveAire Systems. Buyer shall have no right to consequential or incidental damages or to any remedy not hereinbefore described. Any claim by Buyer against CaptiveAire Systems with respect to the goods is deemed waived by Buyer unless submitted to CaptiveAire Systems in writing within ten (10) days of the date Buyer discovered or by reasonable inspection should have discovered, the basis for such claim. Claims Resolution: All claims and disputes between Buyer and CaptiveAire Systems arising out of or relating to performance of any agreement or breach thereof involving this project shall be decided by binding arbitration in accordance with the construction Industry Arbitration rules of the American Arbitration Association (AAA) then existing. Notice of Demand for Arbitration shall be filed in writing by either party to this agreement with the other and with the regional office of the AAA in Charlotte, North Carolina. The procedural and substantive law of the State of North Carolina shall apply in and to all such arbitration proceedings and Raleigh, North Carolina shall be designated as the locale for any such proceedings. Both parties will have the right to conduct discovery in accordance with the Federal Rules of Civil Procedure and within reasonable time limitations to be imposed by the AAA or the arbitrators. Any award arising from such proceedings shall be final and binding upon the parties and enforceable in accordance with the Federal Arbitration Act. Delays: Seller shall not be liable for failures or delays in making delivery hereunder when such failure or delay results from an act of God or the public enemy accident, explosion, fire, storm, earthquake, flood, drought, perils of the sea, strikes, lock-outs, labor troubles, riots, sabotage, embargo, wars (whether or not declared and whether or not the United States is involved), federal, state or municipal law, ordinance, rule, regulation, order license, priority, seizure requisition or allocation or other restrictions, failure or delay of transportation, shortage of or inability to obtain supplies, equipment, fuel or labor or any other circumstances of a similar or different nature beyond the reasonable control of the Seller. Credit: If Buyer's credit, at the sole judgment of the Seller, is impaired at any time, Seller shall have the right to defer shipment or cancel the order. Penalties: No penalty clause of any kind will be effective unless approved in writing by an officer of CaptiveAire Systems. Cancellations: Should the order be cancelled through no fault of CaptiveAire Systems, the Buyer is liable for reimbursement for any and all expenses incurred in connection with this transaction; and in accordance with law for any other losses incurred by Seller. Return of Goods: Please take special care to order carefully and completely. All products purchased are custom orders. Custom orders were manufactured in accordance with customer specifications, and therefore, are only returnable per the terms of our RMA policy (http://www.captiveaire.com/sitedocs/returnpolicy.asp). Verify all information before placing the order. Please review policy with your sales consultant prior to purchasing if you have any questions. Prices: Unless otherwise notified, prices on orders will be held firm provided the order is released for production at time of placement (the date of placement being the date of the Buyer's order). Orders released after 30 days from date of customer's purchase order may be subject to escalation. Title: The title to all material(s) and/or equipment and to any and all additions and accessories thereto and substitutions therefore, shall remain with Seller until the purchase price thereof is paid in full. FORM TC-101 (2/03)